## Table 1
OUTDOOR UNIT DISPLAY (CONT)
Table 30—Outdoor PCB
No. of Presses | Display | Remark
0 | Normal Display | Displays running frequency, running state, or malfunction code
1 | Quantity of indoor units with working connection | Actual Data
|  | Display | Number of Indoor Units
|  | 1 | 1
|  | 2 | 2
|  | 3 | 3
|  | 4 | 4
2 | Outdoor unit running mode code | Off: 0, Fan only: 1, Cooling : 2, Heating : 3, Forced cooling: 4. Forced defrost:A
3 | Indoor unit A capacity | The capacity unit is horse power. If the indoor unit is not connected, the digital display shows the following: "- - " (9K:1HP,12 K:1.2HP,18 K:1.5HP)
4 | Indoor unit B capacity
5 | Indoor unit C capacity
6 | Indoor unit D capacity
7 | Indoor unit E capacity
8 | Indoor unit A capacity demand code | Norm code*HP (9K: 1HP,12 K: 1.2HP,18 K: 1.5HP)
9 | Indoor unit B capacity demand code
10 | Indoor unit C capacity demand code
11 | Indoor unit D capacity demand code
12 | Indoor unit E capacity demand code
13 | Outdoor unit amendatory capacity demand code
14 | The frequency corresponding to the total indoor units' amendatory capacity demand
15 | The frequency after the frequency limit
16 | The frequency sending to compressor control chip
17 | Indoor unit A evaporator outlet temperature (T28 A) | If the temperature is lower than 15.8°F(- 9°C) , the digital display shows "- 9." If the temperature is higher than 158°F (70°C) , the digital display shows "70." If the indoor unit is not connected, the digital display shows: "- - "
18 | Indoor unit B evaporator outlet temperature (T28 B)
19 | Indoor unit C evaporator outlet temperature (T28 C)
20 | Indoor unit D evaporator outlet temperature (T28 D)
21 | Indoor unit E evaporator outlet temperature (T28 E)
22 | Indoor unit A room temperature (T1A) | If the temperature is lower than 32°F (0°C), the digital display shows "0." If the temperature is higher than 122°F (50°C), the digital display shows "50." If the indoor unit is not connected, the digital display shows: "- - "
23 | Indoor unit Broom temperature (T1B)
24 | Indoor unit Croom temperature (T,C)
25 | Indoor unit D room temperature (T1D)
26 | Indoor unit E room temperature (T1E)
27 | Indoor unit A evaporator temperature (T2A) | If the temperature is lower than 15.8°F(- 9°C) , the digital display shows "- 9." If the temperature is higher than 158°F (70°C), the digital display shows "70." If the indoor unit is not connected, the digital display shows: "- - "
28 | Indoor unit B evaporator temperature (T2B)
29 | Indoor unit C evaporator temperature (T2C)
30 | Indoor unit D evaporator temperature (T2D)
31 | Indoor unit E evaporator temperature (T2E)
32 | Condenser pipe temperature (T3)
33 | Outdoor ambient temperature (T4)
34 | Compressor discharge temperature (TP) | The display value is between 86° F- 264.2°F (30°C-129°C). If the temperature is lower than 86°F (30 °C), the digital display shows "30." If the temperature is higher than 210.2°F (99 °C), the digital display shows single and double digits. For example, if the digital display shows "0.5", the compressor discharge temperature is 221° F(105 °C).
35 | AD value of current | The display value is a hex number. For example, the digital display tube shows "Cd", it means AD value is 205.
36 | AD value of voltage
37 | EXV open angle for A indoor unit | Actual data/4. If the value is higher than 99, the digital display shows single and double digits. For example, if the digital display shows "2.0", the EXV open angle is 120 X 4= 480p.
38 | EXV open angle for B indoor unit
39 | EXV open angle for C indoor unit
40 | EXV open angle for D indoor unit
41 | EXV open angle for E indoor unit
42 | Frequency limit symbol | Bit? | Frequency limit caused by IGBT radiator | The display value is a hexadecimal number. For example, the digital display show 2A, then Bit5=1, B it 3= ,1 and Bit1= .1 This means thata frequency limit may be caused by T4, T3, or the current.
|  | Bit6 | Frequency limit caused by PFC
|  | Bit5 | Frequency limit caused by T4.
|  | Bit4 | Frequency limit caused byT 2.
|  | Bit3 | Frequency limit caused by T3.
|  | Bit2 | Frequency limit caused by T5.
|  | Bit1 | Frequency limit caused by current
|  | Bit0 | Frequency limit caused by voltage
43 | Average value of T2 | (Sum T2 value of all indoor units)/(number of indoor units in good connection)
44 | Outdoor unit fan motor state | Off: 0, High speed:1, Med speed: 2, Low speed: 3, Breeze:4, Super breeze: 5
45 | The last error or protection code | 00 means No Malfunction and Protection
46 | F indoor unit capacity
47 | F indoor unit capacity demand code
48 | F indoor unit evaporator outlet temperature (T28 F)
49 | F indoor unit room temperature (T1F)
50 | F indoor unit evaporator temperature (T2F)
51 | EXV open angle for F indoor unit
27