## Sheet1
Infinity/Evolution Zoning Worksheet
Contractor | [5 empty] | Job site
Indoor model |  | 58TNA110C21-20 |  |  |  | Serial
Coil Model |  | CNPHP6024ALA |  |  |  | Serial
Outdoor model |  | 24ANB160A003 |  |  |  | Serial
System Tonnage |  | 5 |  |  |  | Duct Assessment Results
Compressor Stages |  | 2 |  |  |  | Zone 1 | 25% | Zone 5
Number of Zones |  | 4 |  |  |  | Zone 2 | 20% | Zone 6
[6 empty] | Zone 3 | 32% | Zone 7
Zone Airflow Limits | [5 empty] | Zone 4 | 13% | Zone 8
Zone Name | AFL | CFM |  |  |  | leakage | 10% | Total | 100%
Zone 1 | Airflow Limit
Zone Airflow Reference Chart
Zone 2 | Airflow Limit |  |  | Low | Med-Low | Med | Med-High | High | No Limit
|  |  |  | 100% | 138% | 176% | 214% | 250% | X
Zone 3 | Airflow Limit |  | Zone 1
Zone 2
Zone 4 | Airflow Limit |  | Zone 3
Zone 4
Zone 5 | Airflow Limit |  | Zone 5
Zone 6
Zone 6 | Airflow Limit |  | Zone 7
Zone 8
Zone 7 | Airflow Limit
Zone 8 | Airflow Limit
Notes & Formulas
(zone% + leakage%)*(450CFM*# tons)*(zone airflow limit)
Heat Airflow is always calculated off of what the Product Data Sheet Specifies
If DeHum airflow is set to normal then airflow will be based at 275 CFM
If DeHum airflow is set to high then airflow will be based at 325 CFM
2250 CFM Cooling |  |  | 1375 CFM High Cool
875 CFM Low Cool
1475 High Heat |  |  | Lowest speed available for cooling
1320 Low Heat
EXAMPLE 2

## Sheet2
high | 200%
low | 100% | Zone 1 value | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 6 | Zone 7 | Zone 8
Max | 210% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
med | 150%
|  | Capacity per zone, first zone calling | Zone 5: error message
100% |  | Min system capacity | Zone 3: 875; Zone 4: Message?
|  | Zone 1 exists? | Zone 2: Yes; Zone 4: Zone 1 capacity too small to start equipment without other zones calling.; Zone 5: Zone 1 capacity too small to start equipment without other zones calling.
Min Low CFM |  | Zone 2? | Zone 2: Yes; Zone 4: Zone 2 capacity too small to start equipment without other zones calling.; Zone 5: Zone 2 capacity too small to start equipment without other zones calling.
875 |  | Zone 3? | Zone 2: Yes; Zone 4: Zone 3 capacity too small to start equipment without other zones calling.; Zone 5: Zone 3 capacity too small to start equipment without other zones calling.
Min Hi CFM |  | Zone 4? | Zone 2: Yes; Zone 4: Zone 4 capacity too small to start equipment without other zones calling.; Zone 5: Zone 4 capacity too small to start equipment without other zones calling.
1125 |  | Zone 5? | Zone 2: Yes; Zone 4: Zone 5 capacity too small to start equipment without other zones calling.; Zone 5: Zone 5 capacity too small to start equipment without other zones calling.
|  | Zone 6? | Zone 2: Yes; Zone 4: Zone 6 capacity too small to start equipment without other zones calling.; Zone 5: Zone 6 capacity too small to start equipment without other zones calling.
|  | Zone 7? | Zone 2: Yes; Zone 4: Zone 7 capacity too small to start equipment without other zones calling.; Zone 5: Zone 7 capacity too small to start equipment without other zones calling.
|  | Zone 8? | Zone 2: Yes; Zone 4: Zone 8 capacity too small to start equipment without other zones calling.; Zone 5: Zone 8 capacity too small to start equipment without other zones calling.